## Slide 1
June , 30th 2025
June , 30th 2025
Outline
COMMITTEES:
吳有基教授
電氣工程系
導入AI於Monte Carlo分析電力系統韌性: Power System Reliability Assessment Using Monte Carlo OPF Simulation and Fully Connected Neural Network
INTERIM REPORT
BANDUNG
INSTITUT TEKNOLOGI
April,22nd 2026
Smart System lab

## Slide 2
Table of Contents
01
Research Background
Power system reliability, typhoon hazard context
02
Research Objectives
Goals and scope of the study
03
Methodology
Monte Carlo OPF + FCNN pipeline
04
System Description
IEEE 14-bus system & generator data
05
Monte Carlo OPF Results
33,600 simulation runs, EENS analysis
06
FCNN Model & Performance
Architecture, training, R² = 0.9989
07
Line Outage Analysis
Critical line identification
08
ENS Distribution & Survivability
OPF vs FCNN comparison
09
Conclusions & Future Work
Key findings and 6-item roadmap

## Slide 3
Research Background
Context & Motivation
Taiwan faces frequent typhoon events causing widespread transmission outages
Traditional reliability assessment requires computationally expensive AC OPF solves
Energy Not Served (ENS) quantification is critical for grid planning
Real outage data from Taiwan Power Company (Taipower) integrated
Four typhoon events analyzed: Danas, Kong-rey, Gaemi, Krathon
Problem Statement
How can we rapidly estimate ENS across thousands of outage scenarios without re-running full AC OPF every time?
⚡ Typhoon Impact
4 major events
70% FOR in Kong-rey
33,214 scenarios generated
🔢 Computation
33,600 OPF runs
200 weekly samples
100% convergence rate

## Slide 4
Research Objectives
01
Build Monte Carlo OPF Dataset
Generate 33,600 AC OPF solutions across 200 weekly scenarios integrating real typhoon hazard data from Taipower records.
02
Train FCNN Surrogate Model
Develop a Fully Connected Neural Network achieving R² ≥ 0.99 for fast ENS prediction without repeated OPF computation.
03
Critical Line Identification
Identify the most vulnerable transmission lines by outage frequency and ENS contribution (ΔENS analysis).
04
Survivability Assessment
Validate OPF vs FCNN survivability curves at multiple demand thresholds (0.6–1.0 pu), per typhoon scenario.

## Slide 5
03
Methodology
Rexplan pipeline: Julia (PowerModels.jl) + Python (PyTorch)
References:
reXplan Project Team, “reXplan-repo”, GitHub repository. Available: https://github.com/reXplan-project/reXplan-repo
M. Cosovic, “JuliaGrid.jl – Optimal Power Flow API”, Documentation. Available: https://mcosovic.github.io/JuliaGrid.jl/dev/api/optimalPowerFlow/

## Slide 6
Methodology — Two-Stage Pipeline
Excel Input
Generator costs
Typhoon FOR data
▶
Monte Carlo
OPF (Julia)
200 samples
168 hrs each
▶
Dataset
33,214 rows
35 features
+ ENS target
▶
FCNN
Training (Python)
PyTorch
200 epochs
▶
R² = 0.9994
MAE = 0.50 MW
Test set
evaluation
Why Custom Pipeline Instead of reXplan?
Data Incompatibility
reXplan uses European network formats; Taiwan-specific data (NTD cost curves, Taipower FOR) required custom handling
Full OPF Control
Direct use of PowerModels.jl enables custom fictitious generators, VOLL parameterization, and load shedding
Novel FCNN Contribution
reXplan does not support standalone FCNN surrogates trained on custom Monte Carlo datasets
Benchmark Reproducibility
IEEE 14-bus is an internationally standard benchmark enabling direct literature comparison

## Slide 7
04
System Description
IEEE 14-Bus Test System & Generator Data from Taipower

## Slide 8
IEEE 14-Bus System & Generator Configuration
System Specifications
14 Buses
nodes in the network
20 Branches
transmission lines & transformers
5 Generators
at buses 1, 2, 3, 6, 8
11 Load Buses
buses 2,3,4,5,6,9,10,11,12,13,14
259 MW
total base load (100 MVA base)
AC OPF
ACPPowerModel via PowerModels.jl
Seed = 42
full reproducibility guaranteed
Generator Data — Real Taipower Cost Curves
Gen
Bus
Pmax (MW)
Marginal Cost
Plant
Gen 1
1
332.4 MW
1.87 NTD/MWh
協和 #3
Gen 2
2
140.0 MW
2.20 NTD/MWh
協和 #4
Gen 3
3
100.0 MW
2.94 NTD/MWh
林口 #1
Gen 4
6
100.0 MW
3.13 NTD/MWh
林口 #2
Gen 5
8
100.0 MW
3.09 NTD/MWh
林口 #3
C(P) = a·P² + b·P + c (NTD/hr)

## Slide 9
05
Monte Carlo OPF Simulation
33,600 AC OPF runs · 200 weekly scenarios · 4 typhoon events

## Slide 10
Monte Carlo OPF — Simulation Parameters & Typhoon Hazard
Simulation Parameters
Samples (N)
200 weekly scenarios
Hours/sample
168 h (7 days × 24 h)
Total OPF runs
33,600 — all converged
Typhoon share
25% (50 samples)
Formulation
AC OPF (ACPPowerModel)
Solver
Ipopt — interior-point
Load model
±5% Gaussian noise
Random seed
42 (reproducible)
Typhoon Hazard Data (Taipower Records)
Typhoon
Line
Outages
Trans.
Outages
FOR (%)
丹娜絲 Danas
45
6
55.0%
康芮 Kong-rey
90
16
70.0%
凱米 Gaemi
20
4
35.0%
小犬 Krathon
32
8
47.5%
Baseline avg.
—
—
51.9%
Kong-rey = most severe; Gaemi = least severe

## Slide 11
Monte Carlo OPF — Key Results
4,806
MWh/week
EENS (All Scenarios)
5,579
MWh/week (+22.6%)
Typhoon EENS
4,549
MWh/week
Baseline EENS
200/200
samples (100%)
Convergence
Simulation Results Summary
Metric
Value
Note
EENS — all samples
4,806.55 MWh/week
Mean over 200 scenarios
Standard Deviation
4,564.85 MWh/week
High variance under typhoon conditions
EENS — baseline scenarios
4,549.18 MWh/week
Normal operation (150 samples)
EENS — typhoon scenarios
5,578.65 MWh/week
25% typhoon share (50 samples)
Min / Max ENS
0.00 / 16,770.78 MWh
Best week vs worst week

## Slide 12
06
Fully Connected Neural Network
Surrogate model for fast ENS prediction — R² = 0.9994

## Slide 13
FCNN — Architecture & Input Features
Layer Architecture (53,441 parameters)
Input
35
—
—
Hidden 1
256
ReLU
BatchNorm + Dropout 0.2
Hidden 2
128
ReLU
BatchNorm + Dropout 0.2
Hidden 3
64
ReLU
BatchNorm + Dropout 0.2
Hidden 4
32
ReLU
BatchNorm + Dropout 0.2
Output
1
Linear
—
Input Feature Groups (35 total)
🔵 Demand per bus
11 features
Active power demand at each load bus (MW)
🟠 Line status
20 features
Binary: 1 = in service, 0 = outage
🟢 Temporal
2 features
Hour of day (0–23) & day of week (0–6)
🔴 Scenario
2 features
is_typhoon flag + forced outage rate (FOR)
Training Configuration
Framework:
PyTorch (Python 3.10)
Optimizer:
Adam (LR = 1×10⁻³)
LR Scheduler:
ReduceLROnPlateau (patience=10, factor=0.5)
Epochs / Batch:
200 epochs, batch size 256

## Slide 14
FCNN — Model Performance

## Slide 15
FCNN — Model Performance
0.9994
99.94% variance explained
R² Score
0.50 MW
mean absolute error
MAE
0.69 MW
vs ENS range 0–152 MW
RMSE
200/200
OPF samples converged
Convergence
ENS Statistical Comparison — OPF vs FCNN (Test Set: 3,322 Scenarios)
Statistic
OPF (Ground Truth)
FCNN Prediction
Relative Difference
Mean (MW)
28.30
28.43
0.46%
Median (MW)
15.87
15.48
2.46%
Std. Dev. (MW)
29.25
29.05
0.68%
Skewness
1.173
1.175
0.17%
Kurtosis
0.538
0.525
2.42%
Near-perfect agreement across all 5 statistical metrics confirms FCNN fully captures the ENS distribution.

## Slide 16
Line Outage Analysis — Frequency & ENS Contribution
Top 5 Most Frequent Outage Lines
Line 16
57.4%
19,066 hrs
Line 14
56.6%
18,801 hrs
Line 2
54.2%
18,011 hrs
Line 8
54.0%
17,944 hrs
Line 12
53.9%
17,891 hrs
Top 5 Most Critical Lines by ΔENS
Line 4
+18.99 MW
38.61 MW when out
Line 20
+17.10 MW
37.94 MW when out
Line 9
+15.58 MW
36.49 MW when out
Line 14
+14.86 MW
35.39 MW when out
Line 7
+14.81 MW
36.48 MW when out

## Slide 17
Survivability Analysis — OPF vs FCNN
Survivability at Key Demand Thresholds — OPF vs FCNN (3,322 scenarios)
Threshold
Demand Met
OPF Survivability
FCNN Survivability
Agreement
0.60 pu
60%
~98%
~98%
✓ Perfect
0.70 pu
70%
~90%
~90%
✓ Perfect
0.80 pu
80%
71.8%
71.8%
✓ Perfect
0.90 pu
90%
54.7%
54.7%
✓ Perfect
1.00 pu
100%
~0%
~0%
✓ Perfect
Typhoon Scenario Severity Comparison
35.0%
Gaemi
47.5%
Krathon
55.0%
Danas
70.0%
Kong-rey
Forced Outage Rate (FOR)

## Slide 18
09
Conclusions & Future Work
Summary of findings and 6-item research roadmap

## Slide 19
Conclusions — Key Findings
Summary of Key Results
Category
Finding
EENS (all scenarios)
4,806.55 MWh/week
Typhoon vs Baseline
5,578.65 vs 4,549.18 MWh/week → +22.6% under typhoon conditions
FCNN Performance
R² = 0.9994 | MAE = 0.50 MW | RMSE = 0.69 MW — near-perfect accuracy
Most Frequent Outage
Line 16 (57.4% of scenarios)
Most Critical Line (ΔENS)
Line 4 — ΔENS = +18.99 MW
Survivability @ 0.9 pu
54.7% (OPF = FCNN — perfect agreement)
①
Data-Driven Pipeline Works
The complete Monte Carlo OPF + FCNN framework achieves near-perfect ENS prediction (R²=0.9994), enabling fast reliability assessment without repeated OPF runs.
②
Typhoon Impact is Significant
Typhoon scenarios increase EENS by +22.6% vs baseline. Kong-rey (FOR 70%) shows the lowest survivability; Gaemi (FOR 35%) the highest.
③
FCNN = OPF Surrogate Verified
OPF and FCNN survivability curves overlap perfectly at all demand thresholds (0.6–1.0 pu), confirming that FCNN fully preserves reliability characteristics.

## Slide 20
Future Work
01
Generator Outage Analysis (Case 14)
Regenerate dataset with generator status features (gen_bus1,2,3,6,8), expanding to 40 inputs. Retrain FCNN for joint line + generator reliability analysis.
02
Realistic Baseline FOR
Incorporate non-typhoon historical outage data to establish representative baseline FOR (typically 2–10% for transmission lines), replacing the current typhoon-derived 51.9%.
03
Unit Commitment Integration
Extend to Security-Constrained Unit Commitment (SCUC) model incorporating generator startup costs for more accurate total cost and dispatch estimation.
04
Expanded Monte Carlo Dataset
Increase samples from 200 to 1,000+ and add more typhoon events to improve EENS statistical robustness and FCNN generalization across rare extreme scenarios.
05
Real Network Application
Apply the complete framework to a real Taiwanese network topology (Taipower grid) where generator assignments are physically meaningful, replacing the IEEE 14-bus benchmark.
06
reXplan FCNN Integration
Integrate the FCNN surrogate component into reXplan's workflow, combining its robust spatiotemporal hazard modeling with the speed and accuracy of neural network ENS prediction.

## Slide 21
Thank You